3GPP TSG SA WG 1 Meeting #112 	S1-254126

17-21 November 2025, Dallas, Texas, USA	(revision of S1-25xxxx)

Source:	Verizon, EDF, NOVAMINT

pCR Title:	Pseudo-CR on KPI update on Utility Direct Transfer Trip

Draft Spec:	3GPP TR 22.870-V0.4.1

Agenda item:	8.1.8

Document for:	Approval

Contact:	samita.chakrabarti@verizon.com

Abstract: Follow-up FFS on KPI table update for section 11.24 on Utility Direct Transfer Trip protection. This contribution is jointly developed with Electric Power Research Corporation in USA.

1. Introduction

SA1#111 introduced the Utility vertical usecase for fault protection from high voltage to prevent large area power shutdown. The mechanism may be used in other scenarios in electric grid system for fault protection.  The S1-253541 was approved last time with a note for updating the KPI table .

2. Reason for Change

Updating the KPI table in section 11.24 with approximate data available from the Utility companies.

3. Conclusions

<Conclusion part (optional)>

4. Proposal

It is proposed to agree the following changes to the next revision of 3GPP TR 22.870 V0-4.1

* * * First Change * * * *

### 11.24.6	Potential New Requirements needed to support the use case

Editor’s Note: KPI values may  be updated in future contributions

[PR 11.24.6-1] Subject to Operator’s policy, the 6G network shall support end-to-end, secure and reliable IoT device communication with the network following KPI’s in Table 11.24.6-1

[PR 11.24.6-2] Subject to Utility Company and Mobile Operator’s policy, the 6G network should provide alternate means to communicate between devices at both ends in the event when a UE loses its connectivity to the 6G system.

Table 11.24.6-1: KPI for direct trip transfer (DTT) use case

| Profile | Characteristic parameter |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Application Bit rate down link (Kbit/s) | Application Bit rate up link (Kbit/s) | End-to-end latency: maximum (ms) | Payload Message size (byte) | # of UEs connection | Communication service availability: target value | Transfer Interval (ms) |
| Direct Transfer Trip | [50 – 2000] | [50-2000] | [<5 - 10] | [<1500] NOTE | 2 -10 | [> 99.999] | [ 100 ] |
| NOTE: Typical message sizes are 500-byte IEC 61850 [356] Generic Object Oriented Substation Event messages plus any overhead due to tunnelling, security etc. DTT messages are between 2 devices, sometimes they do broadcast to a number of devices. DTT messages are bursty, but they send periodic control messages. |  |  |  |  |  |  |  |

* * * Next Change * * * *

<Proposed change in revision marks>

* * * Next Change * * * *

<Proposed change in revision marks>